## Slide 1: iot.schema.org
Alignment with Brick Schema and Haystack Vocabulary,
Update on Feature of Interest
June 28, 2018

## Slide 2: Alignment with Brick Schema
Haystack vocabulary in iot.schema.org

## Slide 3: Project Haystack
Background:
  Aims to standardize semantic data models to unlock the value of data generated by building equipment.
  It is an open source initiative to enable Internet of Things applications.
  Applications include automation, control, energy, HVAC, lighting, and other environmental systems.
Goal:
  propose a concept to integration Haystack model with iot.schema.org
Review of existing schemas, which provide an RDF/OWL model for Haystack, and a proposal for the integration

## Slide 4: Berkeley-IBM-UVA Model for Haystack
An RDF representation of Haystack tags and tagsets
No schema available
Example:
:ahu rdfs:subClassOf :HaystackMarker;
rdfs:label "AHU"@en;
rdfs:seeAlso <http://project-haystack.org/tag/ahu>;
:usedWith :equip;
:usedWith :rooftop.
:ahu_set rdfs:subClassOf :HaystackMarkerSet;
rdfs:label "AHU set"@en.
:ahu_discharge_air_temp_sensor rdfs:subClassOf :ahu_set;
owl:equivalentClass [ rdf:type owl:Class ; owl:intersectionOf (
[ rdf:type owl:Restriction; owl:onProperty :hasMarker; owl:someValuesFrom :ahu ]
[ rdf:type owl:Restriction; owl:onProperty :hasMarker; owl:someValuesFrom :discharge ]
[ rdf:type owl:Restriction; owl:onProperty :hasMarker; owl:someValuesFrom :air ]
[ rdf:type owl:Restriction; owl:onProperty :hasMarker; owl:someValuesFrom :temp ]
[ rdf:type owl:Restriction; owl:onProperty :hasMarker; owl:someValuesFrom :sensor ]
) ].
Source: https://github.com/arkaaloke/Berkeley-IBM-UVA

## Slide 5: Brick Schema
RDF representation of Haystack tags and tagsets
Brick has additional tags and tagsets
Example:
  brick:AHU_Discharge_Air_Temperature_Sensor
  bf:usesTag
  :AHU,
  :Air,
  :Discharge,
  :Sensor,
  :Supply,
  :Temperature .
Source: http://brickschema.org/

## Slide 6: Brick iot.schema.org Integration
iot:Capability,
iot:FeatureOfInterest
Equipment aligns to iot:FeatureOfInterest and iot:Capability
Example: Boiler equip Boiler as a Capability and FeatureOfInterest

## Slide 7: Brick iot.schema.org Integration
Quantity is missing in Brick schema. A quantity is a measure of an observable phenomenon, that, when associated with something, becomes a property of that thing.
Quantity is missing in Brick.
Point, Measurement, and Quantity align to iot:InteractionPattern
Example: chilled water delta temp sensor  InteractionPattern: ChilledWaterDeltaTemperature (Property)
Quantity
iot:InteractionPattern

## Slide 8: Brick iot.schema.org Integration
iot:DataSchema
Kind
Kind in Haystack defines a tag value type using a predefined string constant.
Kind (DataSchema) is missing in Brick.
For some points kind is missing in Haystack as well.
Kind and Measurement align to iot:DataSchema

## Slide 9: Update: Integration of Haystack vocabulary in iot.schema.org

## Slide 10: Update: Integration of Haystack vocabulary in iot.schema.org
Alignment between sp and Event should be removed
Equip should be aligned with FeatureOfInterest, and new relation should be introduced
“Capability” “isAssociatedWith” “FeatureOfInterest”

## Slide 11: Example
iot:Capability: iot:Boiler
  subclasses: iot:HotWaterBoiler, iot:SteamBoiler, iot:OilBoiler etc
iot:InteractionPattern:
  iot:Action: iot:TurnOn, iot:TurnOff (run cmd)
  iot:Property: iot:RunStatus (run sensor)
  iot:Action: iot:CirculatePumpOn, iot:CirculatePumpOff (circ pump cmd)
  iot:Property: iot:CirculatePumpStatus (circ pump sensor)
  iot:Action: iot:CondensatePumpOn, iot:CondensatePumpOff (condensate pump cmd)
  iot:Property: iot:CondensatePumpStatus (condensate pump sensor)

## Slide 12: Example
:Boiler a owl:Class ;
rdfs:label "Boiler"@en ;
rdfs:subClassOf bf:Tag ;
skos:definition ""@en ;
bf:usedBy brick:Boiler,
brick:Boiler_On_Off_Status,
brick:Boiler_Run_Time_Sensor,
brick:Boiler_Start_Stop_Status .
brick:Boiler_Run_Time_Sensor bf:usesTag :Boiler, :Run, :Sensor, :Time .
Haystack defines more points for a Boiler than present in Brick, e.g. Brick does not define:
  circ pump cmd, circ pump sensor, condensate pump cmd, condensate pump sensor

## Slide 13: Feature of Interest
Update on the meta-model

## Slide 14: Feature Of Interest Pattern

## Slide 15: Thing Description Example
{ "@context": [{"iot": "http://iotschema.org/",
"festoPA":"http://example.com/FestoPA/"} ],
"@type": [ "Thing", "iot:Pump", "iot:Valve", "iot:FloatSwitch", "iot:UltrasonicSensing“ ],
"iot:isAssociatedWith" : {"@id": "festoPA:FESTO-1", "@type": "iot:LiquidMixingSystem"},
"name": "FestoLive",
"id": "urn:dev:wot:siemens:festolive",
"security": [{"scheme": "basic"}],
"properties": {
"PumpStatus": {
"@type": "iot:OperationStatus",
"isPropertyOf": {"@id": "festoPA:Pipe2", "@type": "iot:LiquidPipe"},
"type": "object",
"properties": {"PumpStatus": {"type": "boolean"}},
"writable": false, "observable": false,
"forms": [{ "href": "https://129.144.182.85/iot/api/devices/Festo/PumpStatus",
"mediaType": "application/json“ }] }

## Slide 16: Thank You!
Questions please…